|  | U.S. Department of Labor |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Occupational Safety & Health Administration Top of Form |  |  |  |  |  |  |
|  | www.osha.gov |  | MyOSHA[skip navigational links] | Search | Advanced Search ¦ A-Z Index | Bottom of Form |  |

Construction > Construction Outreach TOC > Common Fire Extinguishing Agents

Construction Safety and Health Outreach Program; U.S. Department of Labor OSHA Office of Training and Education May 1996. Common Fire Extinguishing Agents

- Carbon dioxide - Dry chemical - Multipurpose dry chemical - Halon 1301 - Halon 1211

WATER

- Removes heat - Effective on Class A fires - Inexpensive - Plentiful - Non-toxic Disadvantages: - Conducts electricity - May spread Class B fires - Freezes in cold climates - May carry pollutants as run-off water

CARBON DIOXIDE (CO2)

- Reduces oxygen to less than 15% - Effective on Class B and C fires - No residue - Relatively inert Disadvantages: - Generally >35% concentration by volume required for total flooding system - Toxic to humans at >4% by volume - Not the best agent for smoldering deep-seated fires (maintain concentration for >20 minutes) - Dissipates rapidly - allows reflash - Has a cooling/chilling effect on some electronic components - Vapor density = 1.5 (collects in pits and low areas)

DRY CHEMICAL

- Interrupts chemical reactions - Sodium bicarbonate (baking soda) - Very effective on Class B and C fires - Not considered toxic Disadvantages: - Leaves a residue - Obscures vision - Not good on deep-seated Class A fires - Absorbs moisture and may "cake" within container - May be irritating - Nozzle pressure may cause burning liquids to splash

MULTIPURPOSE DRY CHEMICAL - Interrupts chemical reactions - Ammonium phosphate - Effective on Class A, B, and C fires - Non-conductive Disadvantages: - Obscures vision - More irritating than ordinary dry chemical - Nozzle pressure may cause burning liquids to splash

HALON TERMINOLOGY

Halon 104: Carbon tetrachloride (CCl4) Halon 1211: Bromochlorodifluoromethane (CBrClF2) Halon 1301: Bromotrifluoromethane (CBrF3)

C; F; Cl; Br. 1; 0; 4; -. 1; 2; 1; 1. 1; 3; 0; 1.

> HALON 1301

- Interrupts chemical reactions - Bromotrifluoromethane - Effective on Class A, B, and C fires - Not acutely toxic at <10% by volume - Generally used at <7% by volume - No residue - No chilling effect on electronic parts and components Disadvantages: - Acutely toxic at >10% by volume (anesthetic and cardiac effects) - Delayed effects and effects of chronic exposure not well known - Toxic decomposition products are generated by fire - Vapor density = 5 (collects in pits and low areas) - Production restricted per Montreal Protocol due to depletion of ozone layer

HALON 1301 DECOMPOSITION PRODUCTS

- Hydrogen fluoride (HF) - Hydrogen bromide (HBr) - Bromine (Br2) - Carbonyl Fluoride (COF2) - Carbonyl Bromide (COBr2)

HALON 1211

- Interrupts chemical reactions - Bromochlorodifluoromethane - Effective on Class A, B, and C fires - No residue - May be sprayed (Boiling Point = 25oF) - Used in portable fire extinguishers Disadvantages: - Acutely toxic at >4% by volume (dizziness, impaired coordination and cardiac effects) - Must be used at >5% by volume - Toxic decomposition products are generated by fire - Vapor density = 5.7 (collects in pits and low areas) - Production restricted per Montreal Protocol due to depletion of ozone layer

HALON 1211 DECOMPOSITION PRODUCTS

- Hydrogen bromide (HBr) - Hydrogen chloride (HCl) - Hydrogen fluoride (HF) - Bromine (Br2) - Chlorine (Cl2) - Fluorine (F2) - Carbonyl bromide (COBr2) - Carbonyl chloride (COCl2) - Carbonyl fluoride (COF2)

| Back to Top www.osha.gov |  | www.dol.gov |
| --- | --- | --- |
| Contact Us ¦ Freedom of Information Act ¦ Information Quality ¦ Customer Survey Privacy and Security Statement ¦ Disclaimers |  |  |
| Occupational Safety & Health Administration 200 Constitution Avenue, NW Washington, DC 20210 |  |  |